## Instructions
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Instructions:
Step 1: Input number of transformers in building by KVA on Summary Tab
Step 2: Input cents per KWHr rate on Summary Tab (it will update all sheets)
Step 3: Adjust loading percentage during working and non-working hours as needed
Step 4: Note First Cost is always 0 since this is a retrofit project
Step 5: 30 and 50 Year savings are calculated automatically
Step 6: As energy costs increase - savings will increase. Input percentage that energy is forecasted to increase.
Over past eight years energy costs have increased at a rate of 4.1 % a year.
Notes:
1) Old transformers can be recycled at a rate of 75 cents per pound for copper and 50 cents per pound for Aluminum
2) C3 transformer cost has distributor and contractor mark up and installation included to represent a true end user cost

## Summary
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Project Summary: |  | Input Number of Units | KVA Sizes
|  | 1 | 15 KVA
|  | 1 | 30 KVA
|  | 1 | 45 KVA
|  | 1 | 75 KVA
|  | 1 | 112.5 KVA
|  | 1 | 150 KVA
|  | 1 | 225 KVA
|  | 1 | 300 KVA
|  | 1 | 500 KVA
Input KWhr Rate: | 0.12
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours | [5 empty] | Cost KWh/year
Traditional Transformers* | 28012.0735 | 23.9174 | 23.9174 | 0 | 2010 | 18809.1082 | 18809.1082 |  | 0.12
Acme C3 Transformers | 9202.9653 | 7.8577 | 7.8577 | 0 | 2011 | 19580.2816 | 19580.2816 |  | 0.12492
ANNUAL Energy Savings with Acme C3 | 18809.1082 | 16.0597 | 16.0597 |  | 2012 | 20383.0732 | 20383.0732 |  | 0.13004
[5 empty] | 2013 | 21218.7792 | 21218.7792 |  | 0.13537
Annual kWh savings | 140682.8789 | kWh/year |  |  | 2014 | 22088.7491 | 22088.7491 |  | 0.14092
Avoided Cooling Load | 4.5624 | tons (on peak- normal operation) |  |  | 2015 | 22994.3878 | 22994.3878 |  | 0.1467
(lower losses => less heat to remove) | 4.5624 | tons (off peak - outside normal hours) |  |  | 2016 | 23937.1577 | 23937.1577 |  | 0.15272
[5 empty] | 2017 | 24918.5812 | 24918.5812 |  | 0.15898
Estimated Annual Power Quality Savings | 0 |  |  |  | 2018 | 25940.243 | 25940.243 |  | 0.1655
|  | Life Cycle Operating Cost |  |  | 2019 | 27003.793 | 27003.793 |  | 0.17228
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | 2020 | 28110.9485 | 28110.9485 |  | 0.17934
Traditional Transformers | 0 | 840362.2052 | 1400603.6754 |  | 2021 | 29263.4974 | 29263.4974 |  | 0.1867
Acme C3 Transformers | 68202 | 276088.9594 | 460148.2656 |  | 2022 | 30463.3008 | 30463.3008 |  | 0.19435
Total Life Cycle Savings | -68202 | 564273.2458 | 940455.4097 |  | 2023 | 31712.2961 | 31712.2961 |  | 0.20232
Payback on Incremental Cost | 3.626 | Years |  |  | 2024 | 33012.5003 | 33012.5003 |  | 0.21062
[5 empty] | 2025 | 34366.0128 | 34366.0128 |  | 0.21925
% Increase per Year for Electricity Cost: | 4.1% | 30 years | 50 years |  | 2026 | 35775.0193 | 35775.0193 |  | 0.22824
Total Life Cycle Savings |  | 1072703.2919 | 2961987.2292 |  | 2027 | 37241.7951 | 37241.7951 |  | 0.2376
Payback based on future cost of Electricity | 1.9074 | Years |  |  | 2028 | 38768.7087 | 38768.7087 |  | 0.24734
|  | 35756.7764 |  |  | 2029 | 40358.2258 | 40358.2258 |  | 0.25748
[5 empty] | 2030 | 42012.913 | 42012.913 |  | 0.26804
[5 empty] | 2031 | 43735.4424 | 43735.4424 |  | 0.27903
Summary of Environmental Benefits per Year |  |  |  |  | 2032 | 45528.5956 | 45528.5956 |  | 0.29047
Annual Reduction in Greenhouse Gases | 103.824 | tons of CO2 | 813.9911 | kgs of SO2 | 2033 | 47395.268 | 47395.268 |  | 0.30238
(Per EPA) | 336.4156 | tons of Coal | 350.4411 | kgs of NOx | 2034 | 49338.474 | 49338.474 |  | 0.31477
[5 empty] | 2035 | 51361.3514 | 51361.3514 |  | 0.32768
30 Year Summary of Environmental Benefits |  |  |  |  | 2036 | 53467.1668 | 53467.1668 |  | 0.34111
Annual Reduction in Greenhouse Gases | 3114.7189 | tons of CO2 | 24419.7341 | kgs of SO2 | 2037 | 55659.3207 | 55659.3207 |  | 0.3551
(Per EPA) | 10092.4674 | tons of Coal | 10513.2315 | kgs of NOx | 2038 | 57941.3528 | 57941.3528 |  | 0.36966
[5 empty] | 2039 | 60316.9483 | 60316.9483 | 1072703.2919 | 0.38482
[5 empty] | 2040 |  | 62789.9432 |  | 0.40059
[5 empty] | 2041 |  | 65364.3308 |  | 0.41702
[5 empty] | 2042 |  | 68044.2684 |  | 0.43411
[5 empty] | 2043 |  | 70834.0834 |  | 0.45191
[5 empty] | 2044 |  | 73738.2808 |  | 0.47044
[5 empty] | 2045 |  | 76761.5503 |  | 0.48973
[5 empty] | 2046 |  | 79908.7739 |  | 0.50981
[5 empty] | 2047 |  | 83185.0336 |  | 0.53071
[5 empty] | 2048 |  | 86595.62 |  | 0.55247
[5 empty] | 2049 |  | 90146.0404 |  | 0.57512
[5 empty] | 2050 |  | 93842.0281 |  | 0.5987
[5 empty] | 2051 |  | 97689.5512 |  | 0.62325
[5 empty] | 2052 |  | 101694.8228 |  | 0.6488
[5 empty] | 2053 |  | 105864.3106 |  | 0.6754
[5 empty] | 2054 |  | 110204.7473 |  | 0.70309
[5 empty] | 2056 |  | 114723.1419 |  | 0.73192
[5 empty] | 2057 |  | 119426.7908 |  | 0.76193
[5 empty] | 2058 |  | 124323.2892 |  | 0.79317
[5 empty] | 2059 |  | 129420.544 |  | 0.82569
[5 empty] | 2060 |  | 134726.7864 | 2961987.2292 | 0.85954
Note on B37: For retrofit, enter $ 0
Note on B44: Energy costs have increased over the past 8 years 4.1 % on average per year on a National Average

## 15 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 15.0001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 1 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 14.2501 | 0 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 0 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 0 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 4.9875 | 0 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 4.9875 | 0 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 0 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 0 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 93.5% | 1 | 0 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 97.9%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 607.9762 | 0.51911 | 0.51911
Acme C3 Transformers | 187.5951 | 0.16017 | 0.16017
ANNUAL Energy Savings with Acme C3 | 420.3811 | 0.35893 | 0.35893
Annual kWh savings | 3144.244 | kWh/year
Avoided Cooling Load | 0.10197 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 0.10197 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 18239.2854 | 30398.8091 |  | 15 | 1906
Acme C3 Transformers | 1906 | 5627.8521 | 9379.7535 |  | 30 | 2562
Total Life Cycle Savings | -1906 | 12611.4333 | 21019.0555 |  | 45 | 3322
Payback on Incremental Cost | 4.534 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 2.3205 | tons of CO2 | 18.1926 | kgs of SO2
(Per EPA) | 7.5188 | tons of Coal | 7.8323 | kgs of NOx
Note on B8: Enter the project name.
Note on B11: What is the % loading on your transformers?
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B15: What rate per kWh are you paying the utility?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.

## 30 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 30.0001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 0 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 28.5001 | 1 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 0 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 0 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 9.975 | 0 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 9.975 | 0 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 0 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 0 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 94% | 1 | 0 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 98.3%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 1116.4435 | 0.95325 | 0.95325
Acme C3 Transformers | 302.4884 | 0.25827 | 0.25827
ANNUAL Energy Savings with Acme C3 | 813.9551 | 0.69498 | 0.69498
Annual kWh savings | 6087.9839 | kWh/year
Avoided Cooling Load | 0.19744 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 0.19744 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 33493.3061 | 55822.1769 |  | 15 | 1906
Acme C3 Transformers | 2562 | 9074.653 | 15124.4216 |  | 30 | 2562
Total Life Cycle Savings | -2562 | 24418.6532 | 40697.7553 |  | 45 | 3322
Payback on Incremental Cost | 3.1476 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 4.4929 | tons of CO2 | 35.2251 | kgs of SO2
(Per EPA) | 14.5582 | tons of Coal | 15.1652 | kgs of NOx
Note on B8: Enter the project name.
Note on B11: What is the % loading on your transformers?
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.
Note on B15: What rate per kWh are you paying the utility?

## 45 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 45.0001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 0 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 42.7501 | 0 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 1 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 0 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 14.9625 | 0 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 14.9625 | 0 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 0 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 0 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 95% | 1 | 0 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 98.4%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 1380.8628 | 1.179 | 1.179
Acme C3 Transformers | 426.608 | 0.36425 | 0.36425
ANNUAL Energy Savings with Acme C3 | 954.2548 | 0.81477 | 0.81477
Annual kWh savings | 7137.3567 | kWh/year
Avoided Cooling Load | 0.23147 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 0.23147 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 41425.8852 | 69043.1421 |  | 15 | 1906
Acme C3 Transformers | 3322 | 12798.241 | 21330.4016 |  | 30 | 2562
Total Life Cycle Savings | -3322 | 28627.6443 | 47712.7405 |  | 45 | 3322
Payback on Incremental Cost | 3.4813 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 5.2674 | tons of CO2 | 41.2967 | kgs of SO2
(Per EPA) | 17.0676 | tons of Coal | 17.7792 | kgs of NOx
Note on B8: Enter the project name.
Note on B11: What is the % loading on your transformers?
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.
Note on B15: What rate per kWh are you paying the utility?

## 75 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 75.0001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 0 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 71.2501 | 0 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 0 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 1 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 24.9375 | 0 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 24.9375 | 0 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 0 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 0 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 95.5% | 1 | 0 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 98.6%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 2060.448 | 1.7593 | 1.7593
Acme C3 Transformers | 620.8742 | 0.53012 | 0.53012
ANNUAL Energy Savings with Acme C3 | 1439.5737 | 1.2291 | 1.2291
Annual kWh savings | 10767.3036 | kWh/year
Avoided Cooling Load | 0.34919 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 0.34919 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 61813.4387 | 103022.3979 |  | 15 | 1906
Acme C3 Transformers | 4458 | 18626.2266 | 31043.7111 |  | 30 | 2562
Total Life Cycle Savings | -4458 | 43187.2121 | 71978.6868 |  | 45 | 3322
Payback on Incremental Cost | 3.0968 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 7.9463 | tons of CO2 | 62.2996 | kgs of SO2
(Per EPA) | 25.7479 | tons of Coal | 26.8214 | kgs of NOx
Note on B11: What is the % loading on your transformers?
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on B8: Enter the project name.
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B15: What rate per kWh are you paying the utility?

## 112.5 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 112.5001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 0 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 106.8751 | 0 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 0 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 0 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 37.4063 | 1 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 37.4063 | 0 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 0 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 0 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 96% | 1 | 0 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 98.7%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 2732.9541 | 2.3335 | 2.3335
Acme C3 Transformers | 863.9125 | 0.73763 | 0.73763
ANNUAL Energy Savings with Acme C3 | 1869.0415 | 1.5958 | 1.5958
Annual kWh savings | 13979.5115 | kWh/year
Avoided Cooling Load | 0.45336 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 0.45336 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 81988.6219 | 136647.7031 |  | 15 | 1906
Acme C3 Transformers | 5763 | 25917.3759 | 43195.6265 |  | 30 | 2562
Total Life Cycle Savings | -5763 | 56071.246 | 93452.0766 |  | 45 | 3322
Payback on Incremental Cost | 3.0834 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 10.3169 | tons of CO2 | 80.8855 | kgs of SO2
(Per EPA) | 33.4293 | tons of Coal | 34.823 | kgs of NOx
Note on B8: Enter the project name.
Note on B11: What is the % loading on your transformers?
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.
Note on B15: What rate per kWh are you paying the utility?

## 150 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 150.0001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 0 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 142.5001 | 0 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 0 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 0 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 49.875 | 0 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 49.875 | 1 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 0 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 0 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 96.5% | 1 | 0 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 98.8%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 3171.9253 | 2.7083 | 2.7083
Acme C3 Transformers | 1062.2005 | 0.90693 | 0.90693
ANNUAL Energy Savings with Acme C3 | 2109.7247 | 1.8013 | 1.8013
Annual kWh savings | 15779.7033 | kWh/year
Avoided Cooling Load | 0.51174 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 0.51174 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 95157.7576 | 158596.2627 |  | 15 | 1906
Acme C3 Transformers | 7509 | 31866.016 | 53110.0267 |  | 30 | 2562
Total Life Cycle Savings | -7509 | 63291.7416 | 105486.236 |  | 45 | 3322
Payback on Incremental Cost | 3.5592 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 11.6454 | tons of CO2 | 91.3014 | kgs of SO2
(Per EPA) | 37.7341 | tons of Coal | 39.3072 | kgs of NOx
Note on B8: Enter the project name.
Note on B11: What is the % loading on your transformers?
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.
Note on B15: What rate per kWh are you paying the utility?

## 225 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 225.0001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 0 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 213.7501 | 0 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 0 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 0 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 74.8125 | 0 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 74.8125 | 0 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 1 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 0 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 97% | 1 | 0 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 99%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 4057.1671 | 3.4641 | 3.4641
Acme C3 Transformers | 1325.068 | 1.1314 | 1.1314
ANNUAL Energy Savings with Acme C3 | 2732.0991 | 2.3327 | 2.3327
Annual kWh savings | 20434.7574 | kWh/year
Avoided Cooling Load | 0.66271 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 0.66271 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 121715.0134 | 202858.3557 |  | 15 | 1906
Acme C3 Transformers | 10105 | 39752.0414 | 66253.4024 |  | 30 | 2562
Total Life Cycle Savings | -10105 | 81962.972 | 136604.9534 |  | 45 | 3322
Payback on Incremental Cost | 3.6986 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 15.0809 | tons of CO2 | 118.2355 | kgs of SO2
(Per EPA) | 48.8657 | tons of Coal | 50.903 | kgs of NOx
Note on B8: Enter the project name.
Note on B11: What is the % loading on your transformers?
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.
Note on B15: What rate per kWh are you paying the utility?

## 300 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 300.0001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 0 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 285.0001 | 0 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 0 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 0 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 99.75 | 0 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 99.75 | 0 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 0 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 1 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 97% | 1 | 0 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 99%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 5409.5556 | 4.6188 | 4.6188
Acme C3 Transformers | 1766.7572 | 1.5085 | 1.5085
ANNUAL Energy Savings with Acme C3 | 3642.7984 | 3.1103 | 3.1103
Annual kWh savings | 27246.3401 | kWh/year
Avoided Cooling Load | 0.88361 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 0.88361 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 162286.6666 | 270477.7776 |  | 15 | 1906
Acme C3 Transformers | 14026 | 53002.716 | 88337.86 |  | 30 | 2562
Total Life Cycle Savings | -14026 | 109283.9505 | 182139.9176 |  | 45 | 3322
Payback on Incremental Cost | 3.8503 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 20.1078 | tons of CO2 | 157.6473 | kgs of SO2
(Per EPA) | 65.1543 | tons of Coal | 67.8706 | kgs of NOx
Note on B8: Enter the project name.
Note on B11: What is the % loading on your transformers?
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.
Note on B15: What rate per kWh are you paying the utility?

## 500 KVA
C3 Energy Savings Calculator
Retrofit (Pre TP1 vs C3)
Project Name:
Date:
Data Entry |  |  | Transformers on Project |  |  | Efficiency Comparison
% Load during normal operating hours | 35% | 500.0001 | QTY | kVA | KVA | Pre TP1 (est) | C3
% Load outside operating hours | 35% | Full Load kW | 0 | 15 | 15 | 93.5% | 97.9%
Equipment operating hrs/ day | 12 | 475.0001 | 0 | 30 | 30 | 94% | 98.3%
Equipment operating days/yr | 260 |  | 0 | 45 | 45 | 95% | 98.4%
kWh rate | 0.12 | Load kW | 0 | 75 | 75 | 95.5% | 98.6%
Demand rate ($/kW/mo) ex. $10.00 | 10 | 166.25 | 0 | 112.5 | 112.5 | 96% | 98.7%
Load Power Factor | 0.95 | 166.25 | 0 | 150 | 150 | 96.5% | 98.8%
Cooling System Performance (kW/ton) | 1.75 |  | 0 | 225 | 225 | 97% | 99%
|  | Nonlin Loss Mult | 0 | 300 | 300 | 97% | 99%
Other Transformer Linear Efficiency & Loss Multiplier* | 97.5% | 1 | 1 | 500 | 500 | 97.5% | 99.1%
Acme C3 Efficiency | 99.1%
Energy Cost Analysis (calc) | Annual | kW Losses in | kW Losses outside
| Operating Cost | Normal operation | operating hours
Traditional Transformers* | 7474.741 | 6.3821 | 6.3821
Acme C3 Transformers | 2647.4612 | 2.2605 | 2.2605
ANNUAL Energy Savings with Acme C3 | 4827.2798 | 4.1217 | 4.1217
Annual kWh savings | 36105.6785 | kWh/year
Avoided Cooling Load | 1.1709 | tons (on peak- normal operation)
(lower losses => less heat to remove) | 1.1709 | tons (off peak - outside normal hours)
Estimated Annual Power Quality Savings | 0
Life Cycle Operating Cost
Life Cycle Savings and Payback | First Cost | 30 years | 50 years |  | KVA | C3 K13 CU
Traditional Transformers | 0 | 224242.2302 | 373737.0503 |  | 15 | 1906
Acme C3 Transformers | 18551 | 79423.8373 | 132373.0622 |  | 30 | 2562
Total Life Cycle Savings | -18551 | 144818.3928 | 241363.9881 |  | 45 | 3322
Payback on Incremental Cost | 3.843 | Years |  |  | 75 | 4458
[5 empty] | 112.5 | 5763
[5 empty] | 150 | 7509
[5 empty] | 225 | 10105
[5 empty] | 300 | 14026
[5 empty] | 500 | 18551
Summary of Environmental Benefits
Annual Reduction in Greenhouse Gases | 26.646 | tons of CO2 | 208.9075 | kgs of SO2
(Per EPA) | 86.3397 | tons of Coal | 89.9392 | kgs of NOx
Note on B8: Enter the project name.
Note on B11: What is the % loading on your transformers?
Note on B12: Portion of load that remains on transformer outside of normal operating period as defined above
Note on B13: How many hours a day is your equipment operating?
Note on B14: How many days a year is your facility operating?
Note on B16: Enter the Demand rate being charged by the utility. This is the premium that a Utility charges for peak usage. If Demand rate not known enter $ 0
Note on B17: Enter the Power Factor of the load fed from the transformer (not the building entrance). This varies by application typcially 0.7-0.8 is typical for many 120V electronic loads such as computers. 0.8 is typical of a 3-phase loads or a mixed load environment. Some equipment has internal filtering and in such cases power factor would be in the 0.9 - 0.98 range.
Note on B18: kW per ton of cooling required to offset the transformer losses. Many systems require 1.75 kW per ton of cooling. Very efficient systems may be as low as 1.0 kW/ton 1 ton of cooling = removing heat at the rate of 3.52 thermal kW
Note on C20: Losses increase up to 1.8 times when a conventional transformer is subjected to 120V computer loads. See reference on page 2. Enter a lower loss multiplier such as 1.5 for mixed loads. To compare with just linear load enter a loss multiplier of 1.0
Note on B40: For retrofit, enter $ 0, For upgrade enter the price for the other Transformers. Compare against traditional Copper K13 Transformer.
Note on B41: Enter the price for Acme Electric C3 Copper K13 Transformers.
Note on B15: What rate per kWh are you paying the utility?

## How to Use
How to Use This Calculator
Total kVA of Transformers on Project
Enter the quantity of transformers in the table
Conventional or k-rated Transformer Efficiency
For retrofit projects:
Typical efficiencies for pre TP1 transformers (varies by manufacturer)
15 KVA 93.5%, 30 KVA 94.0%, 45 KVA 95.0%, 75 KVA 95.5%, 112.5 KVA 96.0%, 150 KVA 96.5 %, 225 KVA 97.0%, 300 KVA 97.0%
500 KVA 97.5 %
For new projects:
Typical efficiencies for standard TP1 transformers:
15 KVA 97.0 %, 30 KVA 97.5 %, 45 KVA 97.7 %, 75 KVA 98.0 %, 112.5 KVA 98.2 %, 150 KVA 98.3 %, 225 KVA 98.5 %, 300 KVA 98.6 %
500 KVA 98.7 %
Acme C3 Transformer Efficiency
Enter the efficiency of Acme C3 transformer
15 KVA 97.9 %, 30 KVA 98.3 %, 45 KVA 98.4%, 75 KVA 98.6 %, 112.5 KVA 98.7%, 150 KVA 98.8 %, 225 KVA 99.0%, 300 KVA 99.0%
500 KVA 99.1%
Load Power Factor
Load power factor times load kVA gives the load kW (kW = PF x kVA). Be sure to use the PF of the load fed from the transformer
not at the building entrance. Values range 0.70 to 0.80 for many nonlinear loads. Loads with internal filtering can be over 0.9
Nonlinear load Loss Multiplier
Conventional transformer losses increase by up to 2.7 times when feeding computer type loads.
(IEEE Transactions on Industry Applications, Sept/Oct. ‘96)
“Costs and Benefits of Harmonic Current Reduction for Switch-Mode Power Supplies in a Commercial Office Building”
Tom Key, PEAC, Jih-Sheng Lai, Oak Ridge National Lab, Lockheed Martin Energy Research
The nonlinear load loss multiplier reflects this increase in heat loss, which decreases the net transformer efficiency.
Transformer Operating Losses
Transformer Losses = kW load/net efficiency - kW load.
% load left ON, outside of normal operating hours
Typically 50-70% of normal load remains on during off-hours operation, also transformer remains energized 24hrs/day.
% Additional Cooling
Unlike most substation transformers that are vented to the exterior, most building distribution transformers
are ventilated within the building, and their heat losses therefore add to the cooling load.
Since cooling efficiency varies widely and is typically reflected on additional HVAC load, the energy cost to the transformer
is expressed as a the equivalent % additional cooling kW required to cool a kW of heat. 30-40% is typical
Capital Cost
Cost of transformers. Enter dollar figure for transformers under consideration. If the interest is to look at the justification
for replacing existing transformers, enter $0 in the conventional transformer cost field.
Energy Operating Cost
Energy OPERATING COST (normal op) = (transformer + cooling) kW losses x kWh rate x hrs/day x days/yr + demand charge
Return on Investment (ROI)
ROI on Incremental Cost is based on dividing the Incremental Investment in Acme C3 Transformers by the Annual Savings
ROI on Total Transformer Cost is based on dividing the Total Transformer Cost by the Annual Savings
Environmental Benefits
Conversion rates from kWh to emission reduction and equivalent benefits are published by the EPA,
and reflect environmental benefits derived from reduced emissions associated with reduced power generation.
TERMS OF USE
Acme Electric has used its best efforts in developing the C3 Calculator with the intent of providing an easy
to use and useful calculation tool. However, data entered and assumptions made may not accurately reflect all variables
that apply in a given facility. The results are therefore estimates only and may differ from actual measurements.
The user is responsible for evaluating the suitability and accuracy of the C3 Calculator.
Acme Electric makes no representations or warranties with respect to the accuracy or completeness of the estimates
generated by the C3 Calculator and specifically disclaim any implied warranties of mechantability or fitness for any
particular purpose and shall in no event be liable for any loss of profit or any other commercial damage, including, but not
limited to special, incidental, consequential or other damages.
Toll Free : 1-800-334-5214 or (910) 738-1121